## Horizontal War
5640 Cox Road
Glen Allen, VA 23060
Company: | Chamberlain Mechanical 12535-00 | [6 empty] | Date: | 2014-10-06
Location: | VCU 24223-00
Siegel-02, Commons-01, Sports Med-03
Client Engineer: | George Hardy cell-514-3836 Glenn cell-366-1777 | [6 empty] | bsand11284@yahoo.com
| chamberlainmech@verizon.net |  |  |  | hardygeorge76@gmail.com
s.stanley@chamberlainmech.com
Sample | pH | TDS | Conductivi | BL1821 | P-ALK | M-ALK | CL1455 | C1452SR | Free CL | PUMP SPD
Larricks
UpperHot | 10 | 2687 |  | 700
Upper glycol | 10 | 2767 | [7 empty] | 8 degrees F
Natatorium
Pool | 9.8 | 1469 |  |  | 450 | 450+
Gym | 10.9 | 2592 |  | 800+
Cary St Gym
Hot | 10 | 1552 |  | 800+
Chill | 10.7 | 1453 |  | 600+
Tower | 8.6 | 821 | 1183 |  |  |  | 1.053 |  | 0.2
Hunton Hall | [9 empty] | 35
Hot |  | System under repair |  | per George Hardy
Shaffer Dining
Hot | 9.6 | 780 | 1135 | 600
Commons
Ph1 Hot | 10.3 | 1278 |  | 800+
Ph1 Chill
Ph1 Tower | 8.6 | 614 | 893 |  |  |  |  | 2.1 | 0.2
Ph11 Chill | 10.3 | 808 |  |  | 250 | 450+
Ph11 Tower | OFF
Ph111 Hot | 9.9 | 920 |  |  | 250 | 450+
PH111 Chill | 10.5 | 855 |  |  | 200 | 450+
Sports Med
HP Loop | 10.3 | 1040 |  |  | 400 | 450+
Tower | 8.7 | 829 | 1192 |  |  |  | 0.957 |  |  | 3.5
Siegel Center
Hot | 10.2 | 1411 |  | 800+
2ary Chill | 9.9 | 611 |  |  | 200 | 400
tert Chill | 10.1 | 1008 |  | 600+
Tower | 8.8 | 929 | 1332 |  |  |  | 0.086 |  | 0.25 | 44/100
Chiller Rm AW2000
RMC AW2000
Womens AW2000
045 AW2000
Bow St Parking Deck
Pit
COMMENTS :
Natatorium-Pool loop is tight this month.
Commons PHll-Tower is off.
Commons PHI- Tower is on, solids are in range, added 5lb C1452SR, & 50 (2.5bl) C2189T tablets.
Cary St Gym-Tower treatments are in range, Dosed 10 gallons CL1455, 5 gallons CL2156, & 5 gallons CL49.
Hunton Hall- shot feeder valved OFF & needs replacing asap in order to add treatement.
Recommend water-meter on hot loop make-up for Hunton Hall to monitor water lose!.
Sports Med Tower- controller conductivity & chemical treatments are in range.
Siegel Tower- inhibitor levels are low will order drum, added 40 (2.0lb) C2189 tablets.
Bow Street Pit- Not running.
Chemicals | Amount on Hand |  | Present Pump Setting |  | Recommended Pump Setting |  | Filter Socks, Dates Changed
BL1821
CL4855
CL2156
NaOCL
C1452SR
C2189T
Recommended Limits
| pH | TDS | Conductivi | BL1821 | CL1455 | Chlorine | TDS | C1452SR
Hot | 9.2 - 10.5 | 2000max | 3000max | 600min |  |  | 2000 max
Chill | 9.2 - 10.5 | 2000max | 3000max | 400min |  |  | 2000 max
Dual Temp | 9.2 - 10.5 | 2000max | 3000max | 600min |  |  | 2000 max
Tower | 6.8 - 8.5 |  |  |  | 0.4max | 0.1-0.5 | 925 max | 3.5-4.9
Please contact me with any questions.
Chemtreat Representative : |  | Mark Hudson |  | Phone : | 804-615-5308